# Proposed Change: SECMP0018 - Standard Electricity Distributor Configuration Settings

#### Requirement

This section summarises the key parts of the requirement for this SEC Modification, as currently clarified and refined by the Working Group. The following solution(s) sections detail the required changes to SEC and wider documents that are proposed to implement this requirement. Where there are multiple solutions sections, they reflect the alternatives the Working Group wished to consider.

Context

SMETS requires that ESME are able to record a range of voltage related information and send a range of voltage related Alerts. SMETS also lays out a number of Configuration Data Items that ESME must use to control such voltage related recording.

GBCS specifies Use Cases which allow Electricity Distributors to set the values of the Configuration Data Items. However, GBCS does not specify ‘default values’, to be configured before ESME installation, for these Configuration Data Items, except for the configuration of voltage related Alerts and events. Thus, until configured by an Electricity Distributor, an ESME will report voltage related data on the basis of potentially varying configuration values.

Functional Requirements

This modification is to require in GBCS that ESME:

- Are configured with specified default values for all voltage related and Maximum Demand Configurable Period Configuration Data Items and so have default values for:

Detecting voltage related events; and

Establishing the time period within which the value to be recorded as the Maximum Demand (Configurable Time) Active Power Import value is recorded

as there are no current default values specified in GBCS 2.0 draft 2.

- Have default values for sending voltage related Alerts and logging events than those currently specified in GBCS 2.0 draft 2.

Note that this Modification would be applied to GBCS after BEIS’s CRP 412 and that CRP 412 sets out default values relating to the recording of Events in the Power Event Log and the sending of Alerts via the WAN. Thus, if both this Modification and CRP 412 were to be applied to GBCS at the same TSG Version, the Alert and event default values in this Modification would be reflected in GBCS at that TSG Version. This is the proposers preferred implementation approach.

Note that these default values are different than the equivalent values currently in GBCS and so are not those that will be configured in ESME being built for go-live.

Implementation Obligations

Supplier licences require the installation of ESME that comply with SMETS; SMETS requires that ESME comply with GBCS. Therefore, the GBCS requirement for ESME to have the default configuration values specified in this Modification would be a requirement on Suppliers in relation to ESME they install, which complies with the version of GBCS in to which these changes have been incorporated.

Changes

To deliver the Functional Requirements:

- The voltage related Alert and event default configurations in GBCS section 16.2 would be amended; and

- The other voltage related configuration data items’ default values would be added to GBCS Annex 7 – ‘Data Item Values to be set prior to installation of Devices’

The changes in this Modification would not affect the structure of any of the existing Use Cases, and so do not require changes to DUIS, MMC or DSP systems.

Compatibility

The default configuration values are allowable values at TSG1.0 and so do not give rise to any compatibility issues.

Configuration of events and Alerts as required here will only be fully possible once BEIS CRP412 is incorporated. However, the events in question can be recorded on TSG1.0 Devices and the Alerts in question can be generated by TSG1.0 Devices. Thus, again no compatibility issues arise.

Dependencies

This document is drafted on the basis that CRP412 has been incorporated in to the TSG version in which this Modification is included.

#### Solution

This section details the required changes to SEC and wider documents that are proposed to implement the requirement for this SEC Modification. Please note that all numbering, messages codes, alert codes and so on are based on GBCS 2.0 Draft 2 and related document versions.

SEC main body change

None

SMETS changes

None

CHTS changes

None

GBCS changes

To set the configuration so that, in relation to voltage sag and voltage swell thresholds, no events are recorded and no Alerts produced, set the cells in column F and J of rows 32, 33, 34, 35, 40, 41, 42, 43, 118, 119, 120, 121, 126, 127, 128, and 129 to ‘N’ in Table 16.2 of GBCS. The resulting changes to GBCS Table 16.2 are as in the embedded document:

[DN: updated Table 16.2 to be added by BEIS]

To add the remaining voltage related default configurations, amend GBCS Annex 7 by adding the green highlighted text, rows and table, as follows:

Tables 28a, 28c and 28b lists data items and values that shall be configured in Devices prior to installation.

| Device | Data Item | Reference | Value | Notes |
| --- | --- | --- | --- | --- |
| ESME (all variants) | Maximum Meter Balance Threshold | SMETS 5.7.4.27 | 300,000,000 millipence | NA |
| ESME (all variants) | Randomised Offset Limit | SMETS 5.7.4.33 | 600 seconds | The Randomised Offset [INFO] Is the product of the Randomised Offset Limit(5.7.4.33) and the Randomised Offset Number(5.7.1.5) rounded to the nearest second. This value is used to delay the Tariff Switching Table times, the Auxiliary Load Control Switch switching times, and HAN Connected Auxiliary Load Control Switch switching times |
| ESME (all variants) | RMS Extreme Over Voltage Threshold | SMETS 5.7.4.35 | 265.0 volts | GBCS Use Cases specify a resolution to tenths of volts |
| ESME (all variants) | RMS Extreme Over Voltage Measurement Period | SMETS 5.7.4.34 | 180 seconds | NA |
| ESME (all variants) | RMS Extreme Under Voltage Threshold | SMETS 5.7.4.37 | 190.0 volts | NA |
| ESME (all variants) | RMS Extreme Under Voltage Measurement Period | SMETS 5.7.4.36 | 180 seconds | NA |
| ESME (all variants) | RMS Voltage Sag Threshold | SMETS 5.7.4.40 | 190.0 volts | NA |
| ESME (all variants) | RMS Voltage Sag Measurement Period | SMETS 5.7.4.38 | 180 seconds | NA |
| ESME (all variants) | RMS Voltage Swell Threshold | SMETS 5.7.4.41 | 265.0 volts | NA |
| ESME (all variants) | RMS Voltage Swell Measurement Period | SMETS 5.7.4.39 | 180 seconds | NA |
| ESME (all variants) | (Phase[1]) Average RMS Voltage Measurement Period | SMETS 5.7.4.6 (5.19.1.3) | 1800 seconds | NA |
| ESME (all variants) | (Phase[1]) Average RMS Under Voltage Threshold | SMETS 5.7.4.5 (5.19.1.2) | 212.0 volts | NA |
| ESME (all variants) | (Phase[1]) Average RMS Over Voltage Threshold | SMETS 5.7.4.4 (5.19.1.1) | 258.0 volts | NA |
| Polyphase ESME | Phase[2] Average RMS Voltage Measurement Period | SMETS 5.19.1.3 | 1800 seconds | NA |
| Polyphase ESME | Phase[2] Average RMS Under Voltage Threshold | SMETS 5.19.1.2 | 212.0 volts | NA |
| Polyphase ESME | Phase[2] Average RMS Over Voltage Threshold | SMETS 5.19.1.1 | 258.0 volts | NA |
| Polyphase ESME | Phase[3] Average RMS Voltage Measurement Period | SMETS 5.19.1.3 | 1800 seconds | NA |
| Polyphase ESME | Phase[3] Average RMS Under Voltage Threshold | SMETS 5.19.1.2 | 212.0 volts | NA |
| Polyphase ESME | Phase[3] Average RMS Over Voltage Threshold | SMETS 5.19.1.1 | 258.0 volts | NA |
| ESME (all variants) | Maximum Demand Configurable Time Period: | SMETS 5.7.4.26 |  |  |
|  | - start time |  | 16:00 in hh:mm |  |
|  | - end time |  | 20:00 in hh:mm |  |

Table 28a: Data items and values to be configured prior to installation of Devices

| Data Item | Reference | COSEM class ID | OBIS Code | Attribute ID | Attribute Name | COSEM datatype | Encoded value | Decoded value |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Maximum Meter Balance Threshold | SMETS 5.7.4.27 | 9000 | 0-0:94.44.2.20 | 4 | value_ passive | double-long | 0x11E1A300 | 300,000,000 |
| Randomised Offset Limit | SMETS 5.7.4.33 | 1 | 0-0:94.44.0.1 | 2 | value | long-unsigned | 0x0258 | 600 |
| RMS Extreme Over Voltage Threshold | SMETS 5.7.4.35 | 71 | 0-0:17.0.1.255 | 4 | threshold_normal | double-long-unsigned | 0x00000A5A | 2650 |
| RMS Extreme Over Voltage Measurement Period | SMETS 5.7.4.34 | 71 | 0-0:17.0.1.255 | 6 | min_over_threshold_duration | double-long-unsigned | 0x000000B4 | 180 |
| RMS Extreme Under Voltage Threshold | SMETS 5.7.4.37 | 71 | 0-0:17.0.2.255 | 4 | threshold_normal | double-long-unsigned | 0x0000076C | 1900 |
| RMS Extreme Under Voltage Measurement Period | SMETS 5.7.4.36 | 71 | 0-0:17.0.2.255 | 6 | min_over_threshold_duration | double-long-unsigned | 0x000000B4 | 180 |
| RMS Voltage Sag Threshold | SMETS 5.7.4.40 | 71 | 0-0:17.0.3.255 | 4 | threshold_normal | double-long-unsigned | 0x0000076C | 1900 |
| RMS Voltage Sag Measurement Period | SMETS 5.7.4.38 | 71 | 0-0:17.0.3.255 | 6 | min_over_threshold_duration | double-long-unsigned | 0x000000B4 | 180 |
| RMS Voltage Swell Threshold | SMETS 5.7.4.41 | 71 | 0-0:17.0.4.255 | 4 | threshold_normal | double-long-unsigned | 0x00000A5A | 2650 |
| RMS Voltage Swell Measurement Period | SMETS 5.7.4.39 | 71 | 0-0:17.0.4.255 | 6 | min_over_threshold_duration | double-long-unsigned | 0x000000B4 | 180 |
| (Phase[1]) Average RMS Voltage Measurement Period | SMETS 5.7.4.6 (5.19.1.3) | 7 | 1-0:32.24.0.255 | 4 | capture_period | double-long-unsigned | 0x00000708 | 1800 |
| (Phase[1]) Average RMS Under Voltage Threshold | SMETS 5.7.4.5 (5.19.1.2) | 1 | 1-0:32.31.0.4 | 2 | value | double-long-unsigned | 0x00000848 | 2120 |
| (Phase[1]) Average RMS Over Voltage Threshold | SMETS 5.7.4.4 (5.19.1.1) | 1 | 1-0:32.35.0.4 | 2 | value | double-long-unsigned | 0x00000A14 | 2580 |
| Phase[2] Average RMS Voltage Measurement Period | SMETS 5.19.1.3 | 7 | 1-0:52.24.0.255 | 4 | capture_period | double-long-unsigned | 0x00000708 | 1800 |
| Phase[2] Average RMS Under Voltage Threshold | SMETS 5.19.1.2 | 1 | 1-0:52.31.0.4 | 2 | value | double-long-unsigned | 0x00000848 | 2120 |
| Phase[2] Average RMS Over Voltage Threshold | SMETS 5.19.1.1 | 1 | 1-0:52.35.0.4 | 2 | value | double-long-unsigned | 0x00000A14 | 2580 |
| Phase[3] Average RMS Voltage Measurement Period | SMETS 5.19.1.3 | 7 | 1-0:72.24.0.255 | 4 | capture_period | double-long-unsigned | 0x00000708 | 1800 |
| Phase[3] Average RMS Under Voltage Threshold | SMETS 5.19.1.2 | 1 | 1-0:72.31.0.4 | 2 | value | double-long-unsigned | 0x00000848 | 2120 |
| Phase[3] Average RMS Over Voltage Threshold | SMETS 5.19.1.1 | 1 | 1-0:72.35.0.4 | 2 | value | double-long-unsigned | 0x00000A14 | 2580 |

Table 28b:  DLMS COSEM values to be configured in Devices at manufacture.

| Attribute | COSEM datatype | Tag | Length | Value | Meaning |
| --- | --- | --- | --- | --- | --- |
| entries:entries[1..2] | array | 0x01 | 0x02 |  | An array with two entries, the first turns on monitoring and the second turns it off |
| entries:entries[1]. schedule_table_entry. Index | long-unsigned | 0x12 |  | 0x0001 | The first entry which turns monitoring on |
| entries:entries[1]. schedule_table_entry. enable | boolean | 0x03 |  | 0x01 | True, so the entry always executes |
| entries:entries[1]. schedule_table_entry. script_logical_name | octet-string(6) | 0x09 | 0x06 | 0x00000A8064FF | 0:0-10.128.100.255 which, as per Table 7.3.8, is the script table controlling monitoring |
| entries:entries[1]. schedule_table_entry. script_selector | long-unsigned | 0x12 |  | 0x0001 | Meaning start monitoring at the time in this entry |
| entries:entries[1]. schedule_table_entry. switch_time | octet-string(4) | 0x09 | 0x04 | 0x10000000 | 16:00:00:00 - the time at which monitoring is to turn on |
| entries:entries[1]. schedule_table_entry. validity_window | long-unsigned | 0x12 |  | 0xFFFF | The script is processed at any time after power failure |
| entries:entries[1]. schedule_table_entry. exec_weekdays | bit-string(7) | 0x04 | 0x07 | 0xF8 | 0xF8 = 0b11111000, which means execute this script on Monday to Friday inclusive |
| entries:entries[1]. schedule_table_entry. exec_specdays | bit-string(0) | 0x04 | 0x00 |  | No special day processing |
| entries:entries[1]. schedule_table_entry. begin_date | octet-string(5) | 0x09 | 0x05 | 0xFFFF0A1FFF | 0xFFFF (means any year), 0x0A (means tenth month, so October), 0x1F (means 31st), and 0xFF (means any day of the week) |
| entries:entries[1]. schedule_table_entry. end_date | octet-string(5) | 0x09 | 0x05 | 0xFFFF021CFF | 0xFFFF (means any year), 0x02 (means second month, so February), 0x1C (means 28th), and 0xFF (means any day of the week) |
| entries:entries[2]. schedule_table_entry. index | long-unsigned | 0x12 |  | 0x0002 | The second entry which turns monitoring off |
| entries:entries[2]. schedule_table_entry. enable | boolean | 0x03 |  | 0x01 | True, so the entry always executes |
| entries:entries[2]. schedule_table_entry. script_logical_name | octet-string(6) | 0x09 | 0x06 | 0x00000A8064FF | 0:0-10.128.100.255 which, as per Table 7.3.8, is the script table controlling monitoring |
| entries:entries[2]. schedule_table_entry. script_selector | long-unsigned | 0x12 |  | 0x0002 | Meaning stop monitoring at the time in this entry |
| entries:entries[2]. schedule_table_entry. switch_time | octet-string(4) | 0x09 | 0x04 | 0x14000000 | 20:00:00:00 - the time at which monitoring is to turn off |
| entries:entries[2]. schedule_table_entry. validity_window | long-unsigned | 0x12 |  | 0xFFFF | The script is processed at any time after power failure |
| entries:entries[2]. schedule_table_entry. exec_weekdays | bit-string(7) | 0x04 | 0x07 | 0xFE | 0xFE = 0b11111110, which means execute this script every day |
| entries:entries[2]. schedule_table_entry. exec_specdays | bit-string(0) | 0x04 | 0x00 |  | No special day processing |
| entries:entries[2]. schedule_table_entry. begin_date | octet-string(5) | 0x09 | 0x05 | 0x000001FFFF | From the start of time |
| entries:entries[2]. schedule_table_entry. end_date | octet-string(5) | 0x09 | 0x05 | 0xFFFFFFFFFF | For all time |

Table 28c: Tag, length and values to be populated in attribute 2 of OBIS code 0-0:12.0.0.255 (which relates to the SMETS ‘Maximum Demand Configurable Time Period ‘) to be configured prior to installation of ESME

SEC Appendix E changes

None

DUIS changes

None

MMC changes

None

Other SEC document changes

None

Changes to documents outside of SEC

None

Event configuration is planned to be introduced at GBCS 2.0 by ways of BEIS’ CRP412.