Smart Metering Implementation Programme

Technical Specification Issue Resolution Proposal

This note provides BEIS’s interim position on an issue identified with the current version of the Technical Specifications or their associated content.  Please note this position should be considered as Draft until ratified through TBDG.

| Date | 31 August 2017 |
| --- | --- |
| Issue Resolution Proposal | IRP542 |
| Issues Log ID | TS0760 |
| Issue Title | ECS24 (Read Tariff) clarification for message response |
| Source | DCC |
| Date Raised | 30 June 2017 |
| Status | Draft v0_1 |
| Documentation References | GBCS V1.0 |

Description:

SR 4.11.1 (ECS24) response is failing at head end.

NB. The prior tariff setup, ECS01a has been setup with threshold values all 0.

In the ECS24 response the meter is sending

1) We are setting the ECS24 scaler to be -5 (millipence) which is 0xFB (NB. DLMS Cosem message template says 0x05, but this is not -5)

2) If there are no block thresholds set, we return the block thresholds payload length of 0, which is perfectly allowable by the DLMS Cosem message template.

Please clarify whether the above meter behaviour is acceptable.

We got the following response from Critical:

As defined in Critical's analysis of the payload, the array sizes being returned from the device for Tariff Threshold Matrices are all 0x00. The 1.1.1 sent to set the tariff includes the following

<ThresholdMatrix>

<Thresholds index="1">

<BlockThreshold index="1">0</BlockThreshold>

</Thresholds>

<Thresholds index="2">

<BlockThreshold index="1">0</BlockThreshold>

</Thresholds>

<Thresholds index="3">

<BlockThreshold index="1">0</BlockThreshold>

</Thresholds>

<Thresholds index="4">

<BlockThreshold index="1">0</BlockThreshold>

</Thresholds>

<Thresholds index="5">

<BlockThreshold index="1">0</BlockThreshold>

</Thresholds>

<Thresholds index="6">

<BlockThreshold index="1">0</BlockThreshold>

</Thresholds>

<Thresholds index="7">

<BlockThreshold index="1">0</BlockThreshold>

</Thresholds>

<Thresholds index="8">

<BlockThreshold index="1">0</BlockThreshold>

</Thresholds>

</ThresholdMatrix>

This shows the BlockThresholds being set to 0, which according to DUGIDS is valid. This value of 0 should be held in a single element of the Tariff Threshold Matrix, so number of elements is 1 instead of 0.

Proposed Position:

In relation to thresholds:

- the Tariff Threshold Matrix is defined by SMETS as Configuration Data;

- configuration Data can only be set using Commands sent to Devices, as specified in GBCS. Devices cannot then modify / disregard these settings – rather, the settings have to be used to determine meter processing in line with SMETS;

- in line with SMETS, after the value of a Configuration Data Item on a Device has been set, reading it must return exactly the same value as was set (since the Device cannot modify configuration data).  Thus, for example, if the Tariff Threshold Matrix is set to a matrix containing 24 values all of which are zero, the Device would need to return a matrix containing 24 zero values when the Matrix is read; and

- if no Threshold values have ever been set, the Device will return its factory settings.  These settings should be semantically valid in terms of DLMS COSEM, if they are to avoid parsing errors by other parts of the solution when such defaults are read in Use Cases (so DSP, P&C and other systems used by DCC Users).

Thus, the feedback from Critical appears correct.

On the encoding of the scalar for active tariff price, the ECS24 and ECS24b Use Cases and Message Templates correctly state this is a decimal value of -5 but the Message Templates incorrectly state that its encoded value is 0x05. In line with the A-XDR encoding standards required by DLMS COSEM, -5 should be encoded as a two’s complement value and so should be encoded as 0xFB.

When the DSP receives the correctly encoded value (0xFB) it will accept a value of 0xFB as it is valid DLMS.  DSP does not validate this against the COSEM templates.

If P&C receives an incorrectly encoded value (so any other than 0xFB), it will output an error message.

Thus, the proposed resolution is to correct the ECS24 and ECS24b Message Templates to align the encoding of -5 in the two Responses to 0xFB. This aligns to the standards (DLMS COSEM and A-XDR) and to the DCC systems in live operations.

Interoperability:

This documentation change is to align to DCC systems as they have operated since go-live.

ESME correctly following DLMS COSEM encoding will align to this IRP.

Should any ESME not encode -5 in the way required by DLMS COSEM, P&C will return a corresponding error when parsing ECS24 and ECS24b Responses.

Required Changes to Documentation:

The revised DLMS COSEM Message Templates ECS24 and ECS24b for are embedded below.

| Proposed specification version for incorporation | GBCS V3.0 |
| --- | --- |
| Impact on previous RPs | None |
| Attachment(s) |  |